Project Design Data

2021. 11. 01

CONTENTS

1.	적용범위	3

2.	Site DATA	3

- 적용범위

본 Design Data는 SK 그룹의 에너지 사업 인프라 및 운영 역량을 기반으로, 국내에 친환경 액화수소 충전소를 구축 하는 용역을 위한 Design Data로서 하기의 Data를 기준으로 설계에 적용함.

- Site DATA

  - General Site Data

    - Vibration transmittal precautions	: Yes Earthquake zone in accordance with NFPA 59A

and see 2.1.3, Earthquake data

    - Noise precautions			:  Yes 85dBA(1m form equipment) – TBC

125-140 dBA max for relief valves – TBC

50 dBA at battery limit - TBC

    - Earthquake date

- Operational basis  earthquake (OBE) parameters

Peak ground acceleration 	=	0.063g

Peak ground velocity 	=	Refer to KGS GC203 and Korean

Codes and Standards

Peak ground displacement 	=	Refer to KGS GC203 and Korean

Codes and Standards

- Safe shutdown earthquake (SSE) parameters

Peak ground acceleration 	=	0.154g, 0.22g

Peak ground velocity 	=	Refer to KGS GC203

Peak ground displacement 	=	Refer to KGS GC203

- For equipment items that are designed for SSE, allowable stresses are to be determined in accordance with NFPA-59A, 4-1.3.5 as permitted by UBC 1997, sections 1634.1.2 alternative 2, or 1643.4, where I =1.0 for all items.

  - Wind and Barometer

    - Prevailing direction by height	: NW & WNW

    - Prevailing velocity (mean)		: 2.7 m/sec

    - Design velocity 			: 30 m/sec @ 10m elevation(건축,토목)

45 m/sec @ 10m elevation(기계)

    - Average monthly wind velocity 	: m/s (출처 : 1991~2020년, 기상청)

| Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Wind Vel | 3.2 | 3.4 | 3.6 | 3.4 | 2.8 | 2.4 | 2.6 | 2.4 | 2.1 | 2.4 | 2.9 | 3.3 |

    - Barometric pressure 		: 1024.7 hPa (maximum)

1016.1 hPa (average)

1011.1 hPa (minimum)

    - Change of barometric pressure 	: 9.5 hPa/hr (Rise)

6.2 hPa/hr (Fall)

  - Air Temperatures

    - Maximum summer 		: 38℃

    - Minimum winter			: -19℃

    - Winter design			: -19℃

    - Mean annual			: 11.4℃

    - Average monthly temperatures 	: ℃ (출처 : 1991~2020년,기상청)

| Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Wind Vel | -1.5 | 0.7 | 5.6 | 11.5 | 16.8 | 21.3 | 24.4 | 25.6 | 21.5 | 15.3 | 7.9 | 0.7 |

    - Black  body temperature		: 65 ℃

    - Minimum air relative humidity	: 7.0%

    - Maximum air relative humidity	: 100%

    - Mean air relative humidity		: 68.6%

    - Design relative humidity for cold service : 82%

  - Precipitation

    - Design rainfall

Precipitation shall be calculated  for a 1 in 30 year return period as :

                          

Where In = exponential,	a,b,c,d,e,f,g=factor,	T=period in minutes

    - Design snow loading		: To be determined in accordance with Korean

architectural code

    - Paved area runoff 			: 100%

    - Unpaved area runoff 		: 10%

  - Soil Data

The Soil Data will be reflected in the Detailed Design.

  - Rainfall (출처 : 1991~2020년, 기상청)

    - Maximum				: 337.7mm

    - Average				: 106mm

    - Minimum				: 15.9mm